## Slide 1: Will electrifying transport crash the grid?
EV uptake, charging load and the WA energy transition (Tx / Dx)
SEN Modelling Team | Perth | September 2026
Notes: Open with the question in the title, and give the short answer straight away: no, electrifying transport will not crash the grid, but when vehicles charge matters far more than how many there are.
Three questions structure the talk: (1) does EV uptake overwhelm the WA transition, (2) does it delay the coal exit or lock us into gas, (3) is V2H / V2G essential.
Everything here is for the SWIS / WEM in Western Australia, not the NEM. Main sources: AEMO 2026 WEM ESOO for demand; the AEMO 2025 IASR EV workbook (WEM region, CSIRO 2025 trajectories developed for AEMO) for fleet, energy and charging shapes.
Presenter heads-up: three [placeholder] items remain: the SIREN run on slide 11, and the Western Power feeder and Synergy EV tariff items on slide 13. Fill or cut them before presenting. Slide 21 also has a stray '[1' footnote marker to tidy.

## Slide 2: Will EV uptake overwhelm the WA transition?
01
How many EVs, how much energy, and how does that compare with the SWIS?
Notes: Section 1. Question: will EV uptake overwhelm the WA transition?
Approach: fleet, then energy, then compare with the SWIS. Slides 3 to 5 show the AEMO / CSIRO WEM trajectories. Slide 8 puts them in SWIS context. Slides 9 to 11 test the effect on the system peak in detail.

## Slide 3: Q1 | EV uptake is fast, but it is a forecast, not a surprise
Key takeaway
Total EVs increase 68x at ~15.6% CAGR over the 30-year outlook.
By 2054‑55, Large Residential (28.8%), Medium Residential (24.9%), Large Light Commercial (19.5%) and Small Residential (11.2%) together make up ~85% of the fleet.
Heavy vehicles (trucks, buses) stay under 5% combined.
Large Light Commercial's share of the fleet climbs from ~3.9% in 2030‑31 to ~19.5% by 2054‑55
Chart: WEM Accelerated Transition BEVs by segment, 2025-26–2054-55
| 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55
Large Residential | 9966 | 20146 | 34771 | 52662 | 74371 | 98321 | 124638 | 153206 | 201581 | 249956 | 298331 | 346706 | 395081 | 443457 | 491832 | 540207 | 588582 | 636957 | 685332 | 733708 | 782083 | 830458 | 878833 | 927208 | 975583 | 983800 | 992475 | 1001216 | 1010022 | 1018895
Medium Residential | 20844 | 32610 | 48275 | 66136 | 87262 | 109561 | 133189 | 158068 | 198512 | 238955 | 279399 | 319843 | 360286 | 400730 | 441174 | 481617 | 522061 | 562505 | 602948 | 643392 | 683836 | 724279 | 764723 | 805167 | 845610 | 852863 | 860114 | 867409 | 874746 | 882125
Large Light Commercial | 475 | 1263 | 2477 | 4032 | 5949 | 12053 | 22774 | 38071 | 72738 | 107405 | 142072 | 176739 | 211406 | 246073 | 280740 | 315407 | 350074 | 384742 | 419409 | 454076 | 488743 | 523410 | 558077 | 592744 | 627411 | 639169 | 651179 | 663447 | 675980 | 688782
Small Residential | 18458 | 25410 | 33828 | 42481 | 52287 | 62413 | 72942 | 83845 | 101220 | 118594 | 135969 | 153344 | 170719 | 188094 | 205469 | 222843 | 240218 | 257593 | 274968 | 292343 | 309717 | 327092 | 344467 | 361842 | 379217 | 382550 | 385886 | 389244 | 392624 | 396027
Other segments | 2475 | 4998 | 8562 | 13045 | 18789 | 27366 | 39397 | 54856 | 81584 | 108310 | 135037 | 161765 | 188491 | 215219 | 241946 | 268673 | 295399 | 322127 | 348854 | 375580 | 402307 | 429036 | 455762 | 482489 | 509217 | 517898 | 526755 | 535788 | 545006 | 554409
Source: AEMO, 2025 Inputs, Assumptions and Scenarios Report (IASR), Electric Vehicle workbook, WEM region, Accelerated Transition scenario (CSIRO 2025 EV trajectories developed for AEMO). https://www.aemo.com.au/…/2025-26-inputs-assumptions-and-scenarios.
Notes: This is the Accelerated Transition trajectory for WEM battery EVs, by segment. The fleet grows about 68 times, from roughly 52,000 in 2025-26 to about 3.5 million in 2054-55: a compound growth rate of about 15.6% a year.
The mix: Large Residential, Medium Residential, Large Light Commercial and Small Residential together are about 85% of the fleet by 2054-55. Trucks and buses stay under 5% of the fleet. Large Light Commercial's share climbs from about 3.9% to about 19.5%.
Message: growth is fast, but it is a forecast that planners already carry in their models. It is not a surprise.
Provenance: this is WEM-region data from AEMO's 2025 IASR Electric Vehicle workbook (CSIRO 2025 trajectories developed for AEMO). It is not the NEM 2026 ISP. Slides 4 and 5 use the Slower Growth trajectory, the low end; this slide is the high end. The ESOO's own EV forecast sits closest to the middle one, Step Change.
If asked about today's fleet: WA Department of Transport licensing shows 63,241 light EVs at 30 June 2026 (2.8% of light vehicles). This slide counts battery EVs only; plug-in hybrids are in a separate sheet of the same workbook (about 10,000 to 11,000 in 2025-26).

## Slide 4: Q1 | Even the slow-growth scenario is a ~46x fleet increase by 2055
Key takeaway
Overall growth: total EVs grow from ~47,800 in 2025‑26 to ~2.21M by 2054‑55. Roughly a 46x increase over 30 years (~14% CAGR average).
Growth decelerates over time: early years grow fastest (~37% CAGR 2025‑26→2030‑31), slowing to ~14% CAGR through the middle period and just ~6% CAGR in the final decade (2044‑45→2054‑55)
Residential vehicles dominate but their share erodes: Large/Medium/Small Residential together are ~95% of the fleet in 2025‑26, falling to ~70% by 2054‑55 as commercial and heavy-vehicle segments scale up faster.
Source: AEMO, 2025 Inputs, Assumptions and Scenarios Report (IASR), Electric Vehicle workbook, WEM region, Slower Growth scenario (CSIRO 2025 EV trajectories developed for AEMO). https://www.aemo.com.au/…/2025-26-inputs-assumptions-and-scenarios.
Chart: WEM Slower Growth BEVs by segment, 2025-26–2054-55
| 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55
Articulated Truck | 0 | 0 | 0 | 1 | 2 | 43 | 125 | 245 | 400 | 595 | 830 | 1103 | 1418 | 1770 | 2157 | 2853 | 3548 | 4243 | 4939 | 5634 | 6329 | 7025 | 7720 | 8415 | 9111 | 9806 | 10502 | 11197 | 11892 | 12588
Bus | 35 | 75 | 115 | 160 | 214 | 306 | 437 | 604 | 803 | 1031 | 1283 | 1559 | 1857 | 2175 | 2514 | 2885 | 3256 | 3626 | 3997 | 4368 | 4739 | 5110 | 5481 | 5852 | 6223 | 6594 | 6965 | 7335 | 7706 | 8077
Large Light Commercial | 279 | 646 | 1188 | 1852 | 2643 | 4747 | 8074 | 12489 | 17916 | 24433 | 32004 | 40549 | 50093 | 60540 | 71820 | 90378 | 108935 | 127492 | 146049 | 164606 | 183164 | 201721 | 220278 | 238835 | 257392 | 275949 | 294507 | 313064 | 331621 | 350178
Large Residential | 8720 | 16598 | 27677 | 40923 | 56748 | 72975 | 89771 | 107040 | 124871 | 143302 | 162192 | 181655 | 201690 | 222271 | 243330 | 272711 | 302091 | 331471 | 360852 | 390232 | 419612 | 448993 | 478373 | 507753 | 537134 | 566514 | 595894 | 625275 | 654655 | 684035
Medium Light Commercial | 470 | 814 | 1290 | 1840 | 2477 | 3420 | 4556 | 5833 | 7239 | 8802 | 10520 | 12378 | 14388 | 16530 | 18793 | 22353 | 25914 | 29475 | 33035 | 36596 | 40156 | 43717 | 47278 | 50838 | 54399 | 57959 | 61520 | 65081 | 68641 | 72202
Medium Residential | 19265 | 28689 | 40807 | 54090 | 69459 | 84877 | 100530 | 116342 | 132409 | 148781 | 165335 | 182187 | 199343 | 216787 | 234466 | 258514 | 282563 | 306611 | 330659 | 354708 | 378756 | 402804 | 426853 | 450901 | 474950 | 498998 | 523046 | 547095 | 571143 | 595191
Motorcycle | 1149 | 2311 | 4008 | 6087 | 8627 | 11020 | 13589 | 16325 | 19225 | 22284 | 25498 | 28852 | 32338 | 35948 | 39675 | 45145 | 50615 | 56085 | 61555 | 67025 | 72495 | 77965 | 83435 | 88905 | 94375 | 99845 | 105315 | 110785 | 116255 | 121725
Rigid Truck | 54 | 117 | 168 | 222 | 281 | 615 | 1206 | 2026 | 3049 | 4316 | 5826 | 7565 | 9555 | 11771 | 14206 | 18406 | 22605 | 26805 | 31004 | 35204 | 39403 | 43603 | 47803 | 52002 | 56202 | 60401 | 64601 | 68800 | 73000 | 77199
Small Light Commercial | 406 | 623 | 906 | 1216 | 1569 | 2037 | 2555 | 3098 | 3664 | 4264 | 4899 | 5564 | 6262 | 6987 | 7737 | 8856 | 9974 | 11093 | 12212 | 13331 | 14450 | 15568 | 16687 | 17806 | 18925 | 20044 | 21162 | 22281 | 23400 | 24519
Small Residential | 17426 | 23187 | 29851 | 36292 | 43352 | 50361 | 57414 | 64477 | 71599 | 78805 | 86042 | 93365 | 100777 | 108275 | 115835 | 125958 | 136081 | 146204 | 156327 | 166450 | 176574 | 186697 | 196820 | 206943 | 217066 | 227189 | 237312 | 247435 | 257559 | 267682
Notes: The low case. Even under Slower Growth the WEM battery EV fleet goes from about 47,800 in 2025-26 to about 2.2 million in 2054-55, roughly 46 times, or about 14% a year on average.
Growth decelerates about 37% a year for the first five years, about 14% through the middle period, and about 6% a year in the final decade.
Residential vehicles dominate but their share erodes, from about 95% of the fleet now to about 70% by 2054-55, as commercial and heavy-vehicle segments scale faster.
By 2035-36 this case has about 494,000 battery EVs (about 526,000 including plug-in hybrids). The big multiples come from a small starting base.
Source: AEMO 2025 IASR EV workbook, WEM region, Slower Growth scenario.

## Slide 5: Q1 | EV energy grows ~84x, yet stays a small slice of SWIS consumption
Key takeaway
Total consumption scales up ~84x: from ~103 GWh in 2025‑26 to ~8,630 GWh in 2054‑55, reaching ~1,300 GWh by 2035‑36 (the 10‑year mark).
Consumption by heavy vehicles dominates.
Articulated Trucks and Rigid Trucks are only ~1% of the vehicle fleet by count, but together with Buses they account for ~40% of total energy consumption by 2054‑55, reflecting much higher per-vehicle energy use for freight/heavy vehicles.
Source: AEMO, 2025 Inputs, Assumptions and Scenarios Report (IASR), Electric Vehicle workbook, WEM region, Slower Growth scenario (CSIRO 2025 EV trajectories developed for AEMO). https://www.aemo.com.au/…/2025-26-inputs-assumptions-and-scenarios.
Chart: WEM Slower Growth Total BEV and PHEV load by vehicle type
| 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55
Articulated Truck | 0.001509 | 0.012839 | 0.033424 | 0.082441 | 0.22717 | 3.1805 | 11.6408 | 25.4095 | 44.0123 | 67.4987 | 96.8369 | 130.9476 | 170.6761 | 215.6641 | 266.2897 | 339.33 | 432.9861 | 526.6722 | 621.9855 | 714.009 | 807.772 | 901.459 | 997.7108 | 1088.749 | 1182.4217 | 1276.0881 | 1373.6528 | 1463.4746 | 1557.1795 | 1650.8359
Bus | 1.1024 | 1.011 | 1.7263 | 2.4752 | 3.3556 | 4.6711 | 6.7016 | 9.3538 | 12.6123 | 16.3984 | 20.7662 | 25.4571 | 30.6162 | 36.1564 | 42.1748 | 48.4418 | 55.103 | 61.7687 | 68.6125 | 75.096 | 81.7692 | 88.4343 | 95.3439 | 101.7571 | 108.4213 | 115.085 | 122.0944 | 128.4168 | 135.0838 | 141.7466
Large Light Commercial | 0.80451 | 1.9757 | 3.846 | 6.272 | 9.1891 | 15.0899 | 26.109 | 41.5254 | 61.1095 | 84.8106 | 113.2296 | 144.9934 | 181.0514 | 220.8714 | 264.9268 | 324.249 | 397.9598 | 471.7576 | 546.9748 | 619.2943 | 693.3115 | 767.2228 | 843.064 | 914.4527 | 988.3346 | 1062.0898 | 1139.6071 | 1209.7496 | 1283.5744 | 1357.3304
Large Residential | 20.4806 | 38.8344 | 65.9597 | 99.5616 | 139.2765 | 182.3903 | 226.968 | 271.2662 | 317.0461 | 364.0626 | 415.3158 | 465.5621 | 518.5923 | 573.1386 | 630.8518 | 697.6742 | 776.2943 | 855.3397 | 936.6403 | 1013.0931 | 1092.4931 | 1171.4018 | 1253.5592 | 1328.9889 | 1408.1251 | 1486.9983 | 1570.9807 | 1644.9264 | 1723.8895 | 1802.7656
Medium Light Commercial | 1.2713 | 2.1705 | 3.4544 | 4.9942 | 6.7508 | 9.085 | 12.166 | 15.6392 | 19.5054 | 23.7622 | 28.6584 | 33.8191 | 39.5027 | 45.6009 | 52.226 | 60.7296 | 71.1712 | 81.6296 | 92.3266 | 102.5359 | 113.0295 | 123.5048 | 134.2872 | 144.3619 | 154.833 | 165.2842 | 176.3169 | 186.2091 | 196.6711 | 207.1225
Medium Residential | 43.0097 | 62.8076 | 88.2384 | 116.4913 | 147.6387 | 180.4211 | 213.6922 | 245.8589 | 278.616 | 311.7269 | 348.0832 | 382.9808 | 419.5884 | 456.8674 | 496.1363 | 540.3583 | 592.0649 | 644.0961 | 697.8038 | 747.9043 | 800.1905 | 852.1139 | 906.3866 | 955.7995 | 1007.8889 | 1059.7884 | 1115.3123 | 1163.7143 | 1215.6776 | 1267.5794
Motorcycle | 0.1778 | 0.36681 | 0.66767 | 1.0581 | 1.5357 | 2.0398 | 2.5525 | 3.0841 | 3.6532 | 4.2542 | 4.9097 | 5.5668 | 6.2663 | 6.992 | 7.7644 | 8.6952 | 9.8097 | 10.9295 | 12.0785 | 13.1649 | 14.2894 | 15.4076 | 16.5687 | 17.6408 | 18.7619 | 19.8796 | 21.0658 | 22.1174 | 23.2363 | 24.354
Rigid Truck | 1.8119 | 1.9074 | 3.1584 | 4.2825 | 5.4996 | 9.9439 | 20.3061 | 35.8477 | 56.101 | 81.155 | 112.0557 | 147.541 | 188.6417 | 234.9762 | 286.9869 | 359.9143 | 452.2362 | 544.59 | 638.6131 | 729.2611 | 821.6929 | 914.047 | 1008.9942 | 1098.6708 | 1191.0108 | 1283.3446 | 1379.5928 | 1468.0657 | 1560.4381 | 1652.7619
Small Light Commercial | 1.0313 | 1.5515 | 2.2379 | 3.0108 | 3.8566 | 4.8957 | 6.1506 | 7.4521 | 8.8147 | 10.238 | 11.8372 | 13.4487 | 15.1798 | 16.9885 | 18.9189 | 21.2675 | 24.1092 | 26.9567 | 29.8813 | 32.6484 | 35.5069 | 38.3593 | 41.3062 | 44.0358 | 46.8871 | 49.7323 | 52.7514 | 55.4295 | 58.278 | 61.1233
Small Residential | 32.8348 | 43.0586 | 54.7417 | 66.2449 | 77.8201 | 89.6517 | 101.6375 | 113.022 | 124.613 | 136.2844 | 149.1346 | 161.2461 | 173.9687 | 186.862 | 200.4632 | 215.4481 | 232.9374 | 250.5549 | 268.8165 | 285.6902 | 303.4024 | 320.9757 | 339.4285 | 356.0634 | 373.6991 | 391.2646 | 410.1624 | 426.4417 | 444.0307 | 461.5971
Notes: Now energy rather than vehicle counts, Slower Growth again. EV electricity use grows about 84 times, from about 103 GWh in 2025-26 to about 8,630 GWh by 2054-55. At the 10-year mark, 2035-36, it is about 1,300 GWh.
Heavy vehicles are only about 1% of the fleet by count, but with buses they are about 40% of EV energy by 2054-55, because each one uses far more energy.
Note the chart is battery EV plus plug-in hybrid consumption: the sheet is BEV_PHEV_Consumption, and the chart title now says so.
Why 'small slice': 1.3 TWh is about 5% of the 26.0 TWh the ESOO forecasts for 2035-36 (operational basis). That is the low case. The high case (Accelerated Transition) is about 3.2 TWh, or 12%. Slide 8 shows the range.

## Slide 6: How we used the Siren Model
Smart charging switch
Same energy, different hours
EV Fleet
CSIRO paths
Energy
CSIRO annual kWh
Shape
AEMO, half-hourly profiles
Place
SWIS boundary
Net load
Added to demand
TRACK
Is WA following the forecasts?
Compares Transport WA's real EV numbers with CSIRO's Low / Medium / High projections
EXPLORE
How does EV charging change the grid's path to renewables?
Runs the grid under slow, medium and fast uptake, with smart charging on or off.
Notes: Objectives:
Data inputs:
CSIRO: EV fleet and energy by postcode, in Low, Medium and High scenarios, up to 2050.
AEMO IASR: when EVs charge. The 2025 edition includes a WA profile.
WA Department of Transport: actual registrations, to track actual against projections.
ABS postcode boundaries: to map which postcodes are inside the SWIS.
Outputs:

## Slide 7: Electric vehicle uptake in Western Australia has surged significantly
Key takeaway
63,000+
EVs in WA by June 2026, up 66% from 38,000 a year earlier
1 in 4
new light vehicles licensed in WA in Q2 2026 was an EV, up from about 1 in 9 a year earlier
2.4×
CSIRO's middle forecast: WA had 47,025 EVs at December 2025 against a projected 19,956
Data: CSIRO EV projections by postcode; Transport WA licensing data. Platform: Siren Web.
EV Fleet
Energy
Shape
Place
Net load
Notes: how fast are EVs actually arriving?
Key points:
In less thank 6 years EV adoption in WA has grown from less than 1,400 to more than 63,000 June this year
Where nearly one in four new cars licensed in WA in the June quarter was electric - added about 16,000 EVs in the first six months of this year, nearly double the pace of the six months before.
Chart
compares that growth with the official forecasts
dotted line = Actual (Transport WA's licensing data)
other lines = forecast released by the CSIRO , for AEMO: a slow, expected, and accelerated path.
In all three, eventually nearly every new car sold is electric.
What they disagree on is when, anywhere from the mid-2030s to 2050. And that speed decides how soon the grid has to be ready.

## Slide 8: Q1 | Putting EV load in SWIS context
26.0 TWh
SWIS annual consumption, 2035 (AEMO 2026 WEM ESOO, Expected)
5–12 %
EV share of SWIS consumption, 2035 (1.3 to 3.2 TWh of EV charging)
0.2–0.4 GW
EV load at the evening peak if unmanaged, 2035 (range across scenarios)
Verdict: No. EVs are 5–12% of SWIS consumption in 2035 and draw 0.2–0.4 GW of the ~6.0 GW peak if unmanaged (managed: ~60% less). ESOO already includes ~2 TWh of EV load, so the net effect on the peak is only −2% to +3%. The risk is timing, not volume.
Notes: Three numbers put EV load in SWIS context, all for 2035.
26.0 TWh: SWIS annual consumption in the AEMO 2026 WEM ESOO, Expected scenario (operational basis, 2035-36), up 48% from 17.5 TWh in 2025-26.
5 to 12%: EV charging energy as a share of that, across the three AEMO / CSIRO trajectories: Slower Growth 1.3 TWh (5.0%), Step Change 2.0 TWh (7.7%), Accelerated Transition 3.2 TWh (12.4%).
0.2 to 0.4 GW: the EV load at the time of the system peak (about 6:30 pm) if all charging is unmanaged: 168 MW, 257 MW and 416 MW. Managed charging is about 60% lower (70 to 174 MW). The system peak is about 6.0 GW, the ESOO's 1-in-10 summer peak for 2035-36.
Verdict: no. But read the last sentence: the ESOO already includes about 2 TWh of EV load (its fleet goes from about 68,000 to about 717,000 by 2035-36; households use about 1 TWh), so what a different EV scenario changes is only about minus 2% to plus 3% of the peak. Slide 7 has the workings.
If asked: 'Why not just add EVs to the ESOO?' Because the ESOO forecast already has EVs in it, so that would count EV growth twice.

## Slide 9: Q1 | ESOO Expected plus EV load, 2035
Source: SEN analysis. AEMO 2026 WEM ESOO (Expected, POE10; operational basis derived from underlying); AEMO 2025 IASR EV workbook, WEM region (CSIRO 2025 trajectories: annual energy and charging shapes).
Scenario | Charging | EV energy (GWh) | Share of SWIS use | EV load at system peak (MW) | Net system peak (MW) | Peak vs ESOO | Net minimum (MW)
ESOO 2026 Expected | published | 1,994 | 7.7% | 213 | 6,016 | – | −93
Slower Growth | Unmanaged | 1,301 | 5.0% | 168 | 5,971 | −0.7% | −173
 | Managed | 1,301 | 5.0% | 70 | 5,873 | −2.4% | −248
Step Change | Unmanaged | 1,994 | 7.7% | 257 | 6,060 | +0.7% | −59
 | Managed | 1,994 | 7.7% | 108 | 5,911 | −1.7% | −174
Accelerated Transition | Unmanaged | 3,225 | 12.4% | 416 | 6,219 | +3.4% | 144
 | Managed | 3,225 | 12.4% | 174 | 5,977 | −0.6% | −42
EVs are 5–12% of SWIS energy, yet swapping them into ESOO moves the 2035 peak by only −2% to +3%.
Base: ESOO 2026 Expected, POE10, 2035-36, operational basis: 6,016 MW peak at 6:30 pm, 26.0 TWh (from 32.1 TWh underlying). It already contains ~2.0 TWh of EV charging (IASR Step Change: 2026 ESOO fleet ~717,000 vs 688,000), so each row removes that EV load before adding its own. Share is EV energy over operational consumption. Peak day: Mon 15 Jan 2035 = the 1-in-10 peak day.
Notes: How to read the table. The top row is the ESOO 2026 Expected forecast as published: peak 6,016 MW at about 6:30 pm. It already contains about 1,994 GWh of EV charging, which is about 213 MW at the peak.
Each other row removes that built-in EV load and adds the scenario's instead, so nothing is counted twice. Net system peak is the result. Peak vs ESOO is the change from the published peak.
Results: unmanaged charging moves the peak by minus 0.7%, plus 0.7% and plus 3.4% (Slower Growth, Step Change, Accelerated Transition). Managed charging lowers it by 2.4%, 1.7% and 0.6%. The only case that lifts the peak materially is the high scenario with unmanaged charging, about plus 200 MW.
Net minimum is the lowest demand in the year. The ESOO itself forecasts it going negative (minus 93 MW) as rooftop solar exceeds demand. Unmanaged charging fills the midday trough more than the managed mix, which moves load overnight, so managed rows sit a little lower.
Assumptions to be upfront about: (1) mapping the ESOO Expected case to the IASR Step Change trajectory is our inference: fleet 717,000 vs 688,000, and households' 1 TWh vs 1.1 TWh; (2) the ESOO doesn't publish its charging mix, so we assume the IASR mix of about 70% unmanaged and 30% managed; (3) the 26.0 TWh operational energy is derived from the 32.1 TWh underlying figure, because AEMO publishes only underlying for 2026; (4) the peak day is synthetic (see slides 8 and 9).

## Slide 10: Q1 | Unmanaged charging lifts the peak by up to ~3%
Key takeaway
At the ~6.0 GW peak (about 6:30 pm), unmanaged EVs draw ~170 MW (Slower Growth), ~260 MW (Step Change) and ~420 MW (Accelerated Transition).
ESOO already includes ~210 MW of EV load at the peak, so swapping in each scenario moves the net peak by −0.7%, +0.7% and +3.4%.
Peak day: Mon 15 Jan 2035, the day the synthesised trace reaches the 1-in-10 summer peak. Its shape is 2025's SCADA peak day moved to the same weekday in 2035 – illustrative, not a forecast date.
Source: SEN analysis. AEMO 2026 WEM ESOO (Expected, POE10; operational basis derived from underlying); AEMO 2025 IASR EV workbook, WEM region (CSIRO 2025 trajectories: annual energy and charging shapes). EV load added to a 2035 half-hourly demand trace on the AWST clock, with the EV load already inside ESOO removed first.
Chart: ESOO 2026 Expected, with each EV scenario swapped in, 2035 Unmanaged charging: system demand on the peak day (MW)
| 0 | 2.08333333E-2 | 4.16666667E-2 | 6.25E-2 | 8.3333333300000006E-2 | 0.10416666669999999 | 0.125 | 0.14583333330000001 | 0.16666666669999999 | 0.1875 | 0.20833333330000001 | 0.22916666669999999 | 0.25 | 0.27083333329999998 | 0.29166666670000002 | 0.3125 | 0.33333333329999998 | 0.35416666670000002 | 0.375 | 0.39583333329999998 | 0.41666666670000002 | 0.4375 | 0.45833333329999998 | 0.47916666670000002 | 0.5 | 0.52083333330000003 | 0.54166666669999997 | 0.5625 | 0.58333333330000003 | 0.60416666669999997 | 0.625 | 0.64583333330000003 | 0.66666666669999997 | 0.6875 | 0.70833333330000003 | 0.72916666669999997 | 0.75 | 0.77083333330000003 | 0.79166666669999997 | 0.8125 | 0.83333333330000003 | 0.85416666669999997 | 0.875 | 0.89583333330000003 | 0.91666666669999997 | 0.9375 | 0.95833333330000003 | 0.97916666669999997
ESOO Expected (as published) | 3770 | 3696.9 | 3656.2 | 3587.6 | 3536.3 | 3483.1 | 3445.1 | 3392 | 3391.9 | 3386.9 | 3450.1 | 3457.8 | 3532.4 | 3574.9 | 3637.4 | 3632.5 | 3680.1 | 3687.9 | 3779.8 | 3870.6 | 4016.6 | 4145.6 | 4309 | 4520.2 | 4693.4 | 4891.4 | 4993.2 | 5233.2 | 5410.2 | 5375.7 | 5208.4 | 5186.7 | 5318.9 | 5476.3 | 5645.2 | 5861.1 | 5962.4 | 6015.5 | 5944.1 | 5872.7 | 5810.5 | 5701.1 | 5532.8 | 5321 | 5150.7 | 4962 | 4789.3 | 4632.7
Slower Growth | 3661 | 3587.1 | 3545.5 | 3479.1 | 3429.8 | 3381.2 | 3347.8 | 3298.6 | 3302.4 | 3299.8 | 3365.5 | 3374 | 3449.5 | 3492.2 | 3554.8 | 3551.2 | 3600 | 3609.4 | 3703 | 3792.3 | 3936.8 | 4066.5 | 4230.5 | 4444 | 4619.3 | 4818.4 | 4921.3 | 5162.6 | 5340.8 | 5307.6 | 5141.6 | 5125.1 | 5262.6 | 5426.6 | 5602.1 | 5819.4 | 5922.2 | 5971 | 5895.1 | 5814.3 | 5742.8 | 5624.9 | 5448.2 | 5230.3 | 5053.9 | 4863.4 | 4688.8 | 4528
Step Change | 3727.1 | 3650.2 | 3605.7 | 3534.4 | 3480.3 | 3426.6 | 3388.1 | 3334.7 | 3334.3 | 3330.2 | 3394.3 | 3406.1 | 3484.7 | 3534.5 | 3604.3 | 3611.3 | 3670.7 | 3689.9 | 3793.1 | 3889.1 | 4040.2 | 4173.3 | 4340.9 | 4555.7 | 4732.4 | 4931.8 | 5035 | 5276.9 | 5455.8 | 5423 | 5257.3 | 5239.9 | 5376.4 | 5535.9 | 5706.9 | 5918.3 | 6015.2 | 6060.4 | 5981 | 5899 | 5826.2 | 5705.9 | 5526.9 | 5306.7 | 5128.1 | 4935.6 | 4758.9 | 4596.1
Accelerated Transition | 3844.4 | 3762.4 | 3712.7 | 3632.7 | 3570 | 3507.2 | 3459.6 | 3398.9 | 3391.1 | 3384.2 | 3445.6 | 3463 | 3547.4 | 3609.9 | 3692.3 | 3718.1 | 3796.3 | 3832.9 | 3953.4 | 4061.1 | 4223.9 | 4363.3 | 4537.1 | 4754.3 | 4933.3 | 5133.3 | 5237 | 5480.1 | 5660.2 | 5628 | 5463 | 5443.8 | 5578.6 | 5730.1 | 5893.1 | 6094.1 | 6180.5 | 6219.4 | 6133.8 | 6049.5 | 5974.5 | 5850 | 5666.7 | 5442.6 | 5260.1 | 5063.8 | 4883.6 | 4717.1
Notes: The chart shows system demand on the peak day: the ESOO Expected forecast as published (dark line) and the same day with each EV scenario swapped in, charging unmanaged (plug in on arrival).
The lines nearly overlap. At the 6.0 GW peak (about 6:30 pm), unmanaged EVs draw about 170 MW (Slower Growth), 260 MW (Step Change) and 420 MW (Accelerated Transition). The ESOO already includes about 210 MW, so the net peak moves by minus 0.7%, plus 0.7% and plus 3.4%. Only Accelerated Transition stands out, lifting the evening peak by about 200 MW.
Unmanaged charging peaks mid-afternoon (Unscheduled charging around 3 pm), so it fills the midday trough and also leans into the evening ramp. The net peak stays at about 6:30 pm in all three.
Peak day note: it is Monday 15 January 2035, the day the synthesised trace reaches the 1-in-10 summer peak. Its shape comes from the peak day in 2025's SCADA data, moved to the same weekday in 2035. It is illustrative, not a forecast of that date.
The trace is on Perth (AWST) time, with the EV load already inside the ESOO removed first.

## Slide 11: Q1 | Managed charging keeps the peak below ESOO
Key takeaway
Managed charging (time-of-use, off-peak and solar) draws only ~70, ~110 and ~170 MW at the peak.
Against ESOO's built-in charging mix the net peak falls 2.4%, 1.7% and 0.6%: even the extra energy in Accelerated Transition is charged away from 6:30 pm.
Peak day: Mon 15 Jan 2035, the day the synthesised trace reaches the 1-in-10 summer peak. Its shape is 2025's SCADA peak day moved to the same weekday in 2035 – illustrative, not a forecast date.
Source: SEN analysis. AEMO 2026 WEM ESOO (Expected, POE10; operational basis derived from underlying); AEMO 2025 IASR EV workbook, WEM region (CSIRO 2025 trajectories: annual energy and charging shapes). EV load added to a 2035 half-hourly demand trace on the AWST clock, with the EV load already inside ESOO removed first.
Chart: ESOO 2026 Expected, with each EV scenario swapped in, 2035 Managed charging: system demand on the peak day (MW)
| 0 | 2.08333333E-2 | 4.16666667E-2 | 6.25E-2 | 8.3333333300000006E-2 | 0.10416666669999999 | 0.125 | 0.14583333330000001 | 0.16666666669999999 | 0.1875 | 0.20833333330000001 | 0.22916666669999999 | 0.25 | 0.27083333329999998 | 0.29166666670000002 | 0.3125 | 0.33333333329999998 | 0.35416666670000002 | 0.375 | 0.39583333329999998 | 0.41666666670000002 | 0.4375 | 0.45833333329999998 | 0.47916666670000002 | 0.5 | 0.52083333330000003 | 0.54166666669999997 | 0.5625 | 0.58333333330000003 | 0.60416666669999997 | 0.625 | 0.64583333330000003 | 0.66666666669999997 | 0.6875 | 0.70833333330000003 | 0.72916666669999997 | 0.75 | 0.77083333330000003 | 0.79166666669999997 | 0.8125 | 0.83333333330000003 | 0.85416666669999997 | 0.875 | 0.89583333330000003 | 0.91666666669999997 | 0.9375 | 0.95833333330000003 | 0.97916666669999997
ESOO Expected (as published) | 3770 | 3696.9 | 3656.2 | 3587.6 | 3536.3 | 3483.1 | 3445.1 | 3392 | 3391.9 | 3386.9 | 3450.1 | 3457.8 | 3532.4 | 3574.9 | 3637.4 | 3632.5 | 3680.1 | 3687.9 | 3779.8 | 3870.6 | 4016.6 | 4145.6 | 4309 | 4520.2 | 4693.4 | 4891.4 | 4993.2 | 5233.2 | 5410.2 | 5375.7 | 5208.4 | 5186.7 | 5318.9 | 5476.3 | 5645.2 | 5861.1 | 5962.4 | 6015.5 | 5944.1 | 5872.7 | 5810.5 | 5701.1 | 5532.8 | 5321 | 5150.7 | 4962 | 4789.3 | 4632.7
Slower Growth | 3754.5 | 3688.8 | 3655.4 | 3595 | 3551.8 | 3504.4 | 3472.1 | 3423.4 | 3427.6 | 3423.2 | 3486.9 | 3486.7 | 3553.3 | 3580.1 | 3626.7 | 3597.4 | 3620.4 | 3605.1 | 3673.9 | 3752.1 | 3885.5 | 4006 | 4161 | 4366.8 | 4534.5 | 4730.5 | 4830.3 | 5067.4 | 5241.4 | 5204.7 | 5035.1 | 5009.3 | 5137.5 | 5296.9 | 5467.8 | 5694.8 | 5807.3 | 5873.2 | 5814.6 | 5757 | 5708.7 | 5614.3 | 5461.1 | 5261.3 | 5103.1 | 4921 | 4754.9 | 4607.8
Step Change | 3870.3 | 3806 | 3774.1 | 3712.1 | 3667.3 | 3615.3 | 3578.5 | 3525.9 | 3526.3 | 3519.3 | 3580.5 | 3578.8 | 3643.9 | 3669.2 | 3714.5 | 3682.1 | 3702 | 3683.3 | 3748.6 | 3827.5 | 3961.5 | 4080.7 | 4234.3 | 4437.4 | 4602.3 | 4797 | 4895.5 | 5131 | 5303.4 | 5265.2 | 5094.2 | 5062.4 | 5184.7 | 5337 | 5501 | 5727.3 | 5839 | 5910.6 | 5857.6 | 5811.1 | 5773.9 | 5689.7 | 5546.7 | 5354.3 | 5203.6 | 5023.9 | 4860.3 | 4718.4
Accelerated Transition | 4076.2 | 4014.5 | 3985.1 | 3920.2 | 3872.5 | 3812.5 | 3767.6 | 3708.2 | 3701.6 | 3690.1 | 3746.8 | 3742.4 | 3804.8 | 3827.7 | 3870.6 | 3832.6 | 3846.9 | 3822.1 | 3881.4 | 3961.5 | 4096.7 | 4213.5 | 4364.6 | 4562.8 | 4723 | 4915.3 | 5011.3 | 5244 | 5413.6 | 5372.8 | 5199.1 | 5156.7 | 5268.4 | 5408.4 | 5560 | 5785 | 5895.5 | 5977.1 | 5934.1 | 5907.4 | 5889.9 | 5823.7 | 5698.7 | 5519.6 | 5382.1 | 5206.8 | 5047.5 | 4914.9
Notes: Same chart, managed charging: time-of-use tariffs, off-peak and solar charging. Managed EVs draw only about 70, 110 and 170 MW at the system peak.
Against the ESOO's built-in charging mix, the net peak falls by 2.4%, 1.7% and 0.6%. Even the extra energy in Accelerated Transition is charged away from 6:30 pm: load moves overnight (off-peak and solar charging peaks around 2 am) and to midday.
In the High case the net peak slips a little later, to about 8 pm, as EV load builds in the evening.
The point for the audience: the same vehicles cause a plus 3% or a minus 2% change to the peak depending only on when they charge. That is the case for tariffs and smart chargers (slide 13).
Peak day note: Monday 15 January 2035, the day the synthesised trace hits its 1-in-10 summer peak. Shape taken from 2025's SCADA peak day, moved to the same weekday in 2035. Illustrative, not a forecast date.

## Slide 12: Managed vs Unmanaged Charging
Impacts of Unmanaged Charging
Peak Load Surges
Increases System Costs
Higher Emissions
Benefits of Managed & Smart Charging
Daytime Solar Absorption
Off-Peak Overnight Recovery
Peak Demand Mitigation
Notes: unmanaged charging
Evening Peak Demand: Post-work charging (5:00 PM – 8:00 PM) superimposes directly on household energy use, placing stress on local distribution transformers and suburban feeders
Increases System Costs: Uncontrolled load spikes force grid operators to dispatch expensive gas peaking plants and accelerate network capacity upgrades (rising costs for EV and non-EV owners)
Higher Emissions: Unmanaged charging draws power from fossil-fuel backup generators when solar output is no longer available.
Managed charging
Absorbs Midday Solar Surplus: Shifting charging to daytime hours (9:00 AM – 3:00 PM) absorbs low-cost rooftop solar generation during minimum demand periods.
Off-Peak Overnight Recovery: Scheduling automated charging during quiet overnight hours uses base-load capacity efficiently.
Reduced Peak Demand: Smart charging strategies (such as V1G smart charging) can help flattening system peak demand reduces the need for new peaking infrastructure and battery reserves, helping keep long-term electricity rates stable.
EV energy (2030): Low (Slower Growth) 501 GWh (2.4% of the 20,813 GWh operational base), Medium (Step Change) 670 GWh (3.2%), High (Accelerated Transition) 749 GWh (3.6%).
Peak impact: net of ESOO's own ~670 GWh of embedded EV, unmanaged charging moves the 5,224 MW base peak (6:30 pm) by −7, +15 or +25 MW (−0.1%, +0.3%, +0.5%). Managed charging instead lowers it by 44, 35 or 31 MW (−0.9%, −0.7%, −0.6%) in every scenario.
Coincidence: the change in net peak matches the EV load, net of ESOO's embedded EV, at the base-peak time in every scenario, because the peak interval doesn't shift. That's the headline for unmanaged charging.
The peak doesn't move: it stays at 6:30 pm on 14 January 2030 in all three scenarios (this base scenario has been rebuilt; an earlier version put the peak at 10:30 am on 20 January, from a time-zone bug in the trace since fixed).
Minimum demand: net of ESOO's embedded EV, unmanaged charging moves it by −16, +12 or +25 MW (Low lowers it slightly; Medium and High raise it, easing the minimum-demand and curtailment problem). Managed charging lowers it further in every scenario (−45, −27 or −19 MW).
Integral check is 0.0000%, so the traces conserve energy and the numbers are trustworthy.

## Slide 13: Charging behaviour can lower environmental and financial costs
Stay out of rush hour
Charge with the sun
Give back (V2G)
Source: Australian Electricity Market Operator. “2026 Integrated System Plan (ISP).” June 25, 2026. https://www.aemo.com.au/energy-systems/major-publications/integrated-system-plan-isp/2026-integrated-system-plan-isp.

## Slide 14: Will EVs delay the coal exit or lock us into gas?
02
Demand growth versus the 2029-30 coal retirement and firming needs
Notes: Section 2. Question: will EVs delay the coal exit or lock us into gas?
The framing: the coal retirement date (2029-30 on this slide) is a policy and economics decision. EVs can change how hard the remaining firming has to work, and at which hours, but they don't set the exit date.

## Slide 15: Q2 | Coal exit is driven by policy and economics, not EV demand
What actually sets the coal exit date
State-owned coal retirements (WA Government, 2022): Collie late 2027, Muja D late 2029
Committed firming (ESOO 2026): 1,666 MW of batteries by 2028-29, plus 1,119 MW of generation and storage by 2030-31
Coal units are ageing and increasingly uneconomic in a solar-heavy midday market
What EVs add to that picture
EV energy in 2029-30: 395 GWh (Slower Growth), 491 (Step Change) or 542 (Accelerated Transition), vs SWIS ~19,900 GWh
Charged in daylight, EVs soak up solar that currently forces coal to cycle or curtail
Charged at the evening peak, EVs add to the firming task (committed supply includes 3,127 MW of gas)
Gas is already the swing resource; EVs shift its hours, not its need [placeholder: SIREN run]
Source: WA Government, “State-owned coal power stations to be retired by 2030”, 14 June 2022 (wa.gov.au); AEMO 2026 WEM ESOO (pp. 5, 59, 96); AEMO 2025 IASR EV workbook, WEM region. EV energy is BEV+PHEV; SWIS consumption is ESOO Expected, 2029-30.
Notes: The argument: the coal exit date is set by policy and economics, not by EV demand.
Timetable: the WA Government's June 2022 statement 'State-owned coal power stations to be retired by 2030' gives Collie closing in late 2027 and Muja D in late 2029 (Muja C unit 5 closed in 2022 and unit 6 closes in 2024). The 2026 ESOO models the same dates as 'announced': Collie (317 MW) on 1 October 2027 and Muja D units 7 and 8 (422 MW) on 1 October 2029. The ESOO also assumes Bluewaters (434 MW, privately owned) is unavailable from 1 October 2031. The 2022 statement is old, so cite it alongside the ESOO.
Replacement: the 2022 announcement committed about $3.8 billion of new renewable infrastructure across the SWIS. The ESOO 2026 counts 1,666 MW of existing and committed large-scale batteries by 2028-29 and a further 1,119 MW of committed generation and storage by 2030-31. Coal units are ageing and increasingly uneconomic in a solar-heavy midday market.
What EVs add: EV charging energy in 2029-30 is 395 GWh (Slower Growth), 491 GWh (Step Change) or 542 GWh (Accelerated Transition), against about 19,900 GWh of SWIS consumption (operational basis) in the ESOO Expected case: roughly 2.0% to 2.7%.
Daytime EV charging soaks up solar that currently forces coal to cycle or curtail. Evening charging adds to the firming task: slides 8 and 9 size it at about 170 to 420 MW at the 2035 peak if unmanaged, and 70 to 170 MW if managed. The ESOO's committed supply includes 3,127 MW of gas-fired generators and 1,666 MW of large-scale batteries.
One placeholder remains on this slide: '[placeholder: SIREN run]', which needs an actual run to back the claim that EVs shift the hours gas runs, not the need for it. Say that plainly, or cut the line, until there is a run.

## Slide 16: Q2 | When EVs charge matters more than how much they use
Key takeaway
Articulated Trucks dominate average load by an order of magnitude: averaging ~12–17 kW throughout the day vs. under 3 kW for every other category — reflecting much larger battery/charging capacity for heavy freight vehicles.
All segments share the same daily shape: a trough around 5:00 AM and a peak around 11:00 AM–12:30 PM, then a gradual decline into the evening before rising again — consistent with combined overnight off-peak + midday solar charging patterns rather than a single overnight-only profile.
Articulated Truck ranges from a low of ~7.0 kW (7:00 PM) to a high of ~17.2 kW (11:00AM) — more than double its trough, the widest swing of any category.
Source: AEMO, 2025 Inputs, Assumptions and Scenarios Report (IASR), Electric Vehicle workbook, WEM region (CSIRO 2025 EV trajectories developed for AEMO). https://www.aemo.com.au/…/2025-26-inputs-assumptions-and-scenarios.
Chart: WEM Charging profile by vehicle type
| 0 | 2.0833333333333332E-2 | 4.1666666666666699E-2 | 6.25E-2 | 8.3333333333333301E-2 | 0.104166666666667 | 0.125 | 0.14583333333333301 | 0.16666666666666699 | 0.1875 | 0.20833333333333301 | 0.22916666666666699 | 0.25 | 0.27083333333333298 | 0.29166666666666702 | 0.3125 | 0.33333333333333298 | 0.35416666666666702 | 0.375 | 0.39583333333333298 | 0.41666666666666702 | 0.4375 | 0.45833333333333298 | 0.47916666666666702 | 0.5 | 0.52083333333333304 | 0.54166666666666696 | 0.5625 | 0.58333333333333304 | 0.60416666666666696 | 0.625 | 0.64583333333333304 | 0.66666666666666696 | 0.6875 | 0.70833333333333304 | 0.72916666666666696 | 0.75 | 0.77083333333333304 | 0.79166666666666696 | 0.8125 | 0.83333333333333304 | 0.85416666666666696 | 0.875 | 0.89583333333333304 | 0.91666666666666696 | 0.9375 | 0.95833333333333304 | 0.97916666666666696
Articulated Truck | 12.9287 | 13.0706 | 13.2125 | 13.0647 | 12.917 | 12.5069 | 12.0968 | 11.8591 | 11.6214 | 11.5664 | 11.5113 | 11.8195 | 12.1276 | 12.9735 | 13.8194 | 14.4155 | 15.0116 | 15.4119 | 15.8122 | 16.3103 | 16.8084 | 16.9826 | 17.1568 | 17.0054 | 16.8539 | 16.6643 | 16.4746 | 16.1888 | 15.903 | 15.5716 | 15.2401 | 14.0926 | 12.9452 | 11.2293 | 9.5134 | 8.5677 | 7.6219 | 7.3047 | 6.9876 | 7.5205 | 8.0534 | 8.4458 | 8.8382 | 9.5268 | 10.2155 | 10.6229 | 11.0304 | 11.9795
Bus | 2.0236 | 1.8667 | 1.7098 | 1.515 | 1.3202 | 1.1421 | 0.96395 | 0.8666 | 0.76925 | 0.72897 | 0.68868 | 0.72933 | 0.76998 | 0.9984 | 1.2268 | 1.4341 | 1.6413 | 1.8417 | 2.0421 | 2.1695 | 2.2968 | 2.3642 | 2.4315 | 2.4176 | 2.4038 | 2.3253 | 2.2468 | 2.139 | 2.0313 | 1.9331 | 1.8348 | 1.6647 | 1.4945 | 1.2868 | 1.0792 | 1.0481 | 1.0171 | 1.27 | 1.5229 | 1.8337 | 2.1445 | 2.2697 | 2.3948 | 2.3971 | 2.3995 | 2.269 | 2.1386 | 2.0811
Large Light Commercial | 0.36688 | 0.3445 | 0.32212 | 0.29431 | 0.2665 | 0.23727 | 0.20804 | 0.1842 | 0.16037 | 0.14906 | 0.13776 | 0.15199 | 0.16622 | 0.21523 | 0.26424 | 0.31704 | 0.36985 | 0.42474 | 0.47964 | 0.52129 | 0.56295 | 0.58833 | 0.61372 | 0.61876 | 0.62381 | 0.61453 | 0.60526 | 0.59299 | 0.58072 | 0.56597 | 0.55121 | 0.52191 | 0.4926 | 0.44647 | 0.40034 | 0.37405 | 0.34777 | 0.33575 | 0.32374 | 0.33641 | 0.34908 | 0.35753 | 0.36599 | 0.37921 | 0.39243 | 0.39052 | 0.38862 | 0.37775
Large Residential | 0.27866 | 0.26219 | 0.24571 | 0.22286 | 0.20002 | 0.17591 | 0.15181 | 0.13101 | 0.11021 | 0.09793 | 0.08565 | 0.089971 | 0.094293 | 0.13255 | 0.17082 | 0.20422 | 0.23763 | 0.27631 | 0.315 | 0.34873 | 0.38245 | 0.40385 | 0.42524 | 0.42859 | 0.43193 | 0.42215 | 0.41237 | 0.39688 | 0.38138 | 0.3661 | 0.35082 | 0.31999 | 0.28917 | 0.24926 | 0.20934 | 0.20088 | 0.19242 | 0.19224 | 0.19206 | 0.21239 | 0.23273 | 0.24771 | 0.26269 | 0.27715 | 0.29162 | 0.29296 | 0.2943 | 0.28648
Medium Light Commercial | 0.27723 | 0.26032 | 0.24341 | 0.22239 | 0.20138 | 0.17929 | 0.1572 | 0.13919 | 0.12118 | 0.11264 | 0.1041 | 0.11485 | 0.1256 | 0.16264 | 0.19967 | 0.23957 | 0.27947 | 0.32095 | 0.36243 | 0.39391 | 0.42539 | 0.44457 | 0.46375 | 0.46756 | 0.47137 | 0.46436 | 0.45735 | 0.44808 | 0.43882 | 0.42767 | 0.41652 | 0.39437 | 0.37223 | 0.33737 | 0.30251 | 0.28265 | 0.26278 | 0.25371 | 0.24463 | 0.2542 | 0.26377 | 0.27016 | 0.27655 | 0.28654 | 0.29653 | 0.29509 | 0.29365 | 0.28544
Medium Residential | 0.23141 | 0.21764 | 0.20414 | 0.18516 | 0.16628 | 0.14597 | 0.12613 | 0.10849 | 0.091124 | 0.079902 | 0.06884 | 0.069905 | 0.073993 | 0.10482 | 0.13814 | 0.16321 | 0.19034 | 0.22518 | 0.25857 | 0.28835 | 0.31674 | 0.33455 | 0.35245 | 0.35553 | 0.35851 | 0.3509 | 0.34296 | 0.33025 | 0.31723 | 0.30488 | 0.29241 | 0.26726 | 0.24201 | 0.21082 | 0.17933 | 0.17288 | 0.16353 | 0.16196 | 0.16121 | 0.1781 | 0.19488 | 0.20971 | 0.2222 | 0.2321 | 0.24369 | 0.24444 | 0.24488 | 0.23811
Motorcycle | 0.02264 | 0.021301 | 0.019963 | 0.018107 | 0.016251 | 0.014292 | 0.012334 | 0.010644 | 0.0089542 | 0.0079564 | 0.0069587 | 0.0073098 | 0.0076609 | 0.01077 | 0.013878 | 0.016592 | 0.019306 | 0.022449 | 0.025592 | 0.028332 | 0.031073 | 0.032811 | 0.034549 | 0.034821 | 0.035092 | 0.034298 | 0.033503 | 0.032245 | 0.030986 | 0.029744 | 0.028503 | 0.025998 | 0.023494 | 0.020251 | 0.017008 | 0.016321 | 0.015633 | 0.015619 | 0.015604 | 0.017256 | 0.018908 | 0.020125 | 0.021343 | 0.022518 | 0.023693 | 0.023801 | 0.02391 | 0.023275
Rigid Truck | 2.4629 | 2.2719 | 2.081 | 1.8439 | 1.6068 | 1.39 | 1.1732 | 1.0547 | 0.93623 | 0.8872 | 0.83817 | 0.88764 | 0.93711 | 1.2151 | 1.4931 | 1.7454 | 1.9976 | 2.2415 | 2.4854 | 2.6404 | 2.7954 | 2.8773 | 2.9593 | 2.9424 | 2.9256 | 2.8301 | 2.7345 | 2.6034 | 2.4722 | 2.3527 | 2.2331 | 2.026 | 1.8189 | 1.5662 | 1.3134 | 1.2756 | 1.2379 | 1.5457 | 1.8535 | 2.2317 | 2.61 | 2.7623 | 2.9146 | 2.9175 | 2.9203 | 2.7615 | 2.6028 | 2.5328
Small Light Commercial | 0.24396 | 0.22908 | 0.2142 | 0.19571 | 0.17721 | 0.15778 | 0.13834 | 0.12249 | 0.10664 | 0.09912 | 0.091603 | 0.10107 | 0.11053 | 0.14312 | 0.17571 | 0.21082 | 0.24593 | 0.28244 | 0.31894 | 0.34664 | 0.37434 | 0.39122 | 0.4081 | 0.41145 | 0.41481 | 0.40864 | 0.40247 | 0.39431 | 0.38616 | 0.37634 | 0.36653 | 0.34705 | 0.32756 | 0.29689 | 0.26621 | 0.24873 | 0.23125 | 0.22326 | 0.21528 | 0.2237 | 0.23212 | 0.23774 | 0.24337 | 0.25216 | 0.26095 | 0.25968 | 0.25842 | 0.25119
Small Residential | 0.19053 | 0.17926 | 0.168 | 0.15238 | 0.13676 | 0.12028 | 0.10379 | 0.089574 | 0.075354 | 0.066957 | 0.058561 | 0.061516 | 0.06447 | 0.090631 | 0.11679 | 0.13963 | 0.16247 | 0.18892 | 0.21537 | 0.23843 | 0.26149 | 0.27612 | 0.29075 | 0.29303 | 0.29532 | 0.28863 | 0.28195 | 0.27135 | 0.26076 | 0.25031 | 0.23986 | 0.21879 | 0.19771 | 0.17042 | 0.14313 | 0.13735 | 0.13156 | 0.13144 | 0.13131 | 0.14522 | 0.15912 | 0.16937 | 0.17961 | 0.1895 | 0.19938 | 0.2003 | 0.20122 | 0.19587
Notes: When EVs charge matters more than how much they use. This chart is the average charging power per vehicle across the day, by vehicle type, from the IASR WEM workbook.
Articulated trucks dominate: about 12 to 17 kW on average, against under 3 kW for every other type, because of far larger batteries. Their swing is the widest, from about 7 kW at 7 pm to about 17 kW at 11 am.
All segments share the same daily shape: a trough around 5 am, a peak around 11 am to 12:30 pm, a gradual decline into the evening, then a rise again. That reflects a blend of overnight off-peak and midday solar charging rather than a single overnight profile.
Caution: this is a blend of charging types, including managed ones, which is why it peaks at midday. Unmanaged charging alone is more of an afternoon shape (slides 16 and 19).

## Slide 17: Q2 | Transmission vs distribution: the constraint is local, not system-wide
Transmission (Tx)
Bulk system: EV energy is a modest share of SWIS demand (slides 6–9)
Daytime charging aligns with solar and eases midday minimum-demand problems
Headroom: ESOO 2026 forecasts a shortfall from 2029-30. By 2035-36 the peak capacity target is 7,454 MW vs 5,293 MW existing and committed (−2,161 MW)
Distribution (Dx)
Local: a street of 7 kW chargers at 6 pm can exceed a pole-top transformer rating
Western Power network: [placeholder: % of feeders with evening headroom; Western Power EV / DER data]
Levers: time-of-use tariffs, managed charging, smart chargers [placeholder: Synergy EV tariff uptake]
Source: AEMO, 2026 WEM Electricity Statement of Opportunities, Table 1 (Expected scenario) (aemo.com.au).
Notes: Transmission versus distribution. The bulk system copes (slides 6 to 9); the constraint is local.
Headroom, from the ESOO 2026 Table 1 (Expected scenario): the surplus is small and then turns into a shortfall. Peak Reserve Capacity Target against existing and committed peak capacity: 5,720 vs 5,987 MW in 2026-27 (+267), 6,323 vs 6,670 MW in 2028-29 (+347), then 6,475 vs 6,310 MW in 2029-30 (minus 166), widening to 7,454 vs 5,293 MW in 2035-36 (minus 2,161 MW). Counting anticipated projects, the 2035-36 shortfall is 1,565 MW. Unscheduled operational peak demand is 6,016 MW in 2035-36.
How that fits with EVs: the EV effect on the peak is about minus 145 to plus 200 MW (minus 2.4% to plus 3.4%), well inside a shortfall of 1.6 to 2.2 GW. EVs don't cause the shortfall. But the gap between unmanaged and managed charging in the high scenario is about 240 MW, which is not trivial against 596 MW of anticipated capacity. So charging behaviour matters most where headroom is thin.
Distribution is where it bites: a street of 7 kW chargers all starting at 6 pm can exceed a pole-top transformer's rating even when the SWIS as a whole has plenty of headroom. System-level numbers can't show that.
Levers: time-of-use tariffs, managed charging and smart chargers. Slide 9 shows what they are worth at system level. The ESOO 2026 adds a related point: it models Synergy's VPP for the first time, with about 640 MW of distributed batteries coordinated in 2028-29 (at a 50% availability assumption) reducing the peak by about 200 MW.
Two placeholders remain and are not in the ESOO: the share of Western Power feeders with evening headroom (needs Western Power EV / DER data) and Synergy EV tariff uptake. Fill them from those sources or cut them.

## Slide 18: Is V2H / V2G essential, or a techno-utopia?
03
Vehicle-to-home, vehicle-to-grid, and what smart charging alone can do
Notes: Section 3. Question: is V2H / V2G essential, or a techno-utopia?
Framing: before asking for bidirectional charging, look at what smart one-way charging can already do. Slides 8 and 9 showed it cuts the peak impact by about 60%. The next slides define the charging types, then weigh V2G's proven benefits against its promises.

## Slide 19: Unmanaged versus managed EV charging
unmanaged
Arrival-based charging (e.g. "Unscheduled", "Public"). Peaks in the afternoon/evening as people get home or park — the worst case for the system peak.
managed
Time-of-use, off-peak or coordinated charging (e.g. "Off-peak and Solar", "TOU Grid Solar"). Shifts load to the middle of the day (solar) or overnight.
v2x
Vehicle-to-home / vehicle-to-grid. Includes bi-directional charging
Notes: Definitions used in the modelling. These are AEMO's IASR charging-type categories, grouped into three modes.
Unmanaged: arrival-based charging (Unscheduled and Public). It peaks in the afternoon and evening as people get home or park, so it is the worst case for the system peak.
Managed: time-of-use, off-peak or coordinated charging (Off-peak and Solar, TOU Grid Solar). It shifts load to the middle of the day or to overnight.
V2X: vehicle-to-home and vehicle-to-grid, including bidirectional charging.
Slides 7 to 9 use the unmanaged and managed modes; V2X is not modelled yet.

## Slide 20: EV charging Profiles
Region: WEM Source: AEMO IASR EV workbook (2025), 2040 snapshot, BEV_PHEV_Charge_Type (%) / BEV_PHEV_Profile_kW
Charging Type | Mode | Share | Weekday Peak | Weekend Peak
Of-peak and Solar Charging | Managed | 0.152 | 02:00 | 02.00
TOU Grid Solar Charging | Managed | 0.052 | 12:00 | 12:00
Unscheduled Charging | Unmanaged | 0.364 | 15:00 | 15:00
Public Charging | Unmanaged | 0.112 | 12:00 | 12:00
Vehicle to Grid – vehicle charging | V2x | 0.063 | 12:00 | 13:00
Vehicle to Home – vehicle charging | V2x | 0.063 | 12:00 | 13:30
Notes: AEMO's assumed mix of charging types for the WEM, from the 2040 snapshot in the IASR workbook: Unscheduled 36.4% (peaks 3 pm), Public 11.2% (peaks midday), Off-peak and Solar 15.2% (peaks 2 am), TOU Grid Solar 5.2% (peaks midday), and V2G and V2H at 6.3% each (peak around midday).
The shares shown add up to about 81%. The remainder is charging types without a static time-of-day profile, such as dynamic time-of-use, so it is not on this table.
In our modelling, unmanaged is Unscheduled plus Public (47.6% of all charging) and managed is Off-peak and Solar plus TOU Grid Solar (20.4%). That is about 70% and 30% once normalised, which is the mix we assume for the EV load already inside the ESOO.
Source: BEV_PHEV_Charge_Type (%) and BEV_PHEV_Profile_kW sheets, WEM region.

## Slide 21: Weekday Charging Shapes
Notes: Weekday charging shape by charging type: the share of a day's charging energy in each half-hour.
Unscheduled charging (red) is broad from about 9 am to 4 pm and still elevated through the evening. Public charging peaks around midday. Off-peak and Solar (green dotted) is highest overnight, around 2 am. TOU Grid Solar peaks at midday.
The V2G and V2H lines (purple) peak between 11 am and noon, fall from mid-afternoon and are down to about a quarter of their peak by 5 pm, so they stay off the evening peak.
The point: only the unmanaged types keep charging through the 5 to 7 pm window.

## Slide 22: Weekend Charging Shapes
Notes: Weekend charging shapes. Very similar timing to weekdays.
The V2G and V2H shapes stay high for longer, from about 11 am to 3 pm, then fall away sharply from about 3 pm to 5 pm. Unscheduled charging peaks in the mid to late afternoon.
Weekends matter less for the system peak, which is a summer weekday evening, but the shapes show the same principle: managed and V2X charging avoid the early evening.

## Slide 23: Composite Weekday Charging Shapes
Notes: The composite shapes, weighted by each charging type's share, are what feed the EV load model in slides 7 to 9.
Unmanaged (red): a trough around 5 am, rising through the morning to a plateau from about 11 am to 4 pm, then easing through the evening. It is still well above its trough at 6 pm.
Managed (green): highest overnight, declining through the day to a trough between about 5 and 6 pm, then climbing again after 8 pm. That evening trough is why managed charging cuts the coincident peak load by about 60% compared with unmanaged.
This is the visual answer to 'when, not how much'.

## Slide 24: Q3 | V2G: what is proven
The case for "essential"
Fleet battery by 2035-36: ~494,000 to ~991,000 BEVs (IASR WEM) x 75.8 kWh average = ~37 to ~75 GWh of on-board storage. For scale, large-scale batteries committed by 2028-29 total 1,666 MW (ESOO 2026)
Cars sit parked ~95% of the time, mostly at home or work
V2H gives households outage resilience without a separate battery
Trials: Horizon Power's 12-month V2G trial in Exmouth (to September 2025): four V2G-capable Nissan Leafs with local organisations, coordinated by a DERMS. No kW or revenue figures published
Source: AEMO 2025 IASR EV workbook, WEM region (BEVs, Slower Growth to Accelerated Transition); AEMO 2026 WEM ESOO; WA Government, “Two-way EV charging trial delivers success”, 22 September 2025 (wa.gov.au); Compare the Market, EV battery evolution: 75.8 kWh is the 2026 average of 20 available models, not a fleet average (comparethemarket.com.au).
Notes: Q3 is split over three slides: what is proven, what is promised, and what it costs. This one is what is proven.
Cars are parked about 95% of the time, mostly at home or work, so the energy is there to use. V2H gives households outage resilience without a separate battery.
Scale: the IASR WEM workbook has about 494,000 (Slower Growth), 650,000 (Step Change) and 991,000 (Accelerated Transition) battery EVs in 2035-36. At 75.8 kWh each that is about 37, 49 and 75 GWh of on-board storage. Read that as a theoretical ceiling, not usable V2G capacity: the 75.8 kWh comes from Compare the Market's 2026 average of 20 available EV models. It is not a fleet average and not weighted by sales, and the article doesn't say whether it includes plug-in hybrids. A real 2035 fleet will hold many older, smaller-battery cars (the same article puts the 2011 average at 18.1 kWh) plus some larger trucks and buses. Usable capacity is lower again once you allow for state-of-charge limits, cars not being plugged in, and the share of cars that are V2G-capable.
For comparison the ESOO 2026 counts 1,666 MW of existing and committed large-scale batteries by 2028-29, but gives power, not energy, so the slide does not state a stationary GWh figure. The only duration in the ESOO is the ERA's 200 MW / 1,200 MWh (six-hour) benchmark battery. If you want a ratio, get the registered MWh of those batteries first, rather than assuming a duration.
Trial: Horizon Power's 12-month V2G trial in Exmouth, completed in September 2025. Four organisations (the Gascoyne Development Commission, the Shire of Exmouth, the Exmouth Chamber of Commerce and Industry, and WA Country Health Service) received V2G-capable Nissan Leafs, coordinated by a distributed energy resource management system (DERMS) that balanced grid stability with customer needs. The Government's media statement (22 September 2025) reports success but publishes no kW, revenue or participation figures, so don't quote any. Horizon Power says it will use the findings to develop products that let customers get more from their EVs.
Broader evidence that coordinated storage works: the ESOO 2026 cites a July 2025 California event where over 100,000 aggregated batteries cut peak demand by an average of 539 MW, and a June 2024 New England event where batteries, EVs and loads cut it by 375 MW. Those are batteries and VPPs, not mainly V2G.

## Slide 25: Q3 | V2G: what is promised
The developing standards
Inverter Standards Core V2G Inverter Standard: AS4777.2 See Clean Energy Council (CEC) Approved Product List,
Vehicle-to-Charger Historically the older CHAdeMO natively support bi-directional power. Australia has now transitioned to ISO 15118-20. This standard governs bidirectional energy transfer using the standard CCS2 plug (the dominant charging standard in Australia).
Grid Integration - The WA Government utilizes the Common Smart Inverter Profile Australia (CSIP-AUS), which is based on the IEEE 2030.5 protocol. This allows utilities to Orchestrate EV charging and discharging during peak demand periods. [1
Notes: What is promised: V2G depends on standards and grid integration being in place. The slide lists them.
Inverter: the core V2G inverter standard is AS4777.2; check products against the Clean Energy Council approved product list.
Vehicle to charger: older CHAdeMO connectors natively support bidirectional power. Australia has moved to ISO 15118-20, which governs bidirectional energy transfer over the CCS2 plug, the dominant connector here.
Grid integration: the WA Government uses CSIP-AUS (Common Smart Inverter Profile Australia), based on the IEEE 2030.5 protocol. It lets utilities orchestrate EV charging and discharging during peak periods.
The point for the audience: the standards exist, so the open questions are product availability, warranties and network connection rules, and whether owners will plug in and be willing to discharge. Only the Exmouth trial is local evidence so far (slide 20).
Tidy before presenting: the slide ends with a stray '[1' footnote marker, and the Clean Energy Council link is a google.com redirect rather than a direct link. Both look like pasted artefacts.

## Slide 26: Q3 | V2G: what is the cost
The case for "techno-utopia"
Bidirectional chargers cost ~$5k to $10k+ plus installation $1.5k to $3k
Smart one-way charger from ~$800, typically $1.2k to $1.9k, plus installation $500 to $2k
Managed (one-way) charging captures most of the grid benefit at a fraction of the cost
Source: Solar Choice, Bidirectional EV chargers explained (V2G, V2H and V2L) (solarchoice.net.au); Solar Choice, EV charger price index (solarchoice.net.au). 2026 prices; installation varies by site.
Notes: What it costs. Bidirectional chargers are about $5,000 to $10,000 or more for the hardware, plus $1,500 to $3,000 for installation by a licensed electrician: roughly $6,500 to $13,000 or more installed. A smart one-way charger starts at about $800 and is typically $1,200 to $1,900, with premium units near $3,000, plus $500 to $2,000 to install: roughly $1,300 to $3,900 installed.
That is about three to five times the cost. Against that, managed one-way charging already captures most of the grid benefit: slides 8 and 9 show it cutting the peak impact by about 60%.
Source: Solar Choice's bidirectional charger guide and EV charger price index, 2026. These are ranges, and installation varies with switchboard condition, cable distance and location. Solar Choice expects bidirectional prices to fall as more models arrive in 2026. It also names only a few options as clearly available to homeowners in early 2026 (V2Grid Numbat, Sigenergy and RedEarth Boomerang), which fits the 'still maturing' point on slide 21.
Presenter flag: I could only read search summaries of the Solar Choice pages, not the pages themselves. Check the figures against the live pages before presenting.
Bridge to the verdict: V2G is an upside to plan for, not a dependency.

## Slide 27: Q3 | V2G-Key: a possible low-cost route
A future option to watch
V2G-Key, from Merge Energy, aims to bring V2G to everyday EV owners “at a fraction of the cost of today’s bidirectional chargers”
Backers include UNSW, Amber, RACE for 2030, TRaCE and the AEA (Australia’s Economic Accelerator)
Status: in development. Customer trials and pre-sale registration are open; no price, vehicle compatibility or standards are published
Company claim: an EV battery stores more than three times the energy of most home batteries, without export limits or risk to the car’s warranty
Until it is priced, tested and accepted by car makers, treat it as an upside to watch, not a plan
Source: V2G-Key by Merge Energy (v2gkey.com), viewed September 2026. Cost and performance statements are the company's claims; no price or specification is published.
Notes: This follows the cost slide and asks whether the cost barrier could fall. V2G-Key is a candidate: it is a company's claim about a product in development, so present it as an option to watch, not a fact.
What the company says (v2gkey.com): V2G-Key is from Merge Energy and lets EV owners use their car's battery to support their home and the grid. It will be available 'at a fraction of the cost of today's bidirectional chargers'; it calls itself 'the most affordable storage-for-solar'. It says an EV battery stores 'more than three times the energy of most home batteries' and offers 'peace of mind without export limits or jeopardising your EV battery's warranty'. Backers listed are UNSW, TRaCE, the AEA, Amber and RACE for 2030.
What the site does not say: no price, no list of compatible vehicles, no standards (such as AS4777.2 or ISO 15118-20, slide 21), and it doesn't say whether it is a charger, an adapter or something else. It is in development; owners can register interest for customer trials and pre-sale.
Other material I found by search says the project has had an AEA Ignite grant, CSIRO Renewable Energy Integration Facility support, and has validated ISO 15118-20 and ISO 15118-2 communications and controlled power flows between charger, vehicle, inverter and home or grid. I couldn't trace those to a primary source, so they are deliberately not on the slide. Check them before you say them.
Against the cost slide: bidirectional chargers are roughly $6,500 to $13,000 or more installed, against about $1,300 to $3,900 for a smart one-way charger. 'A fraction of the cost' would matter. Until there is a price, a compatibility list and trial results, it doesn't change the verdict: V2G is an upside to plan for, not a dependency.
What to watch: a published price, which vehicles and chargers it works with, conformance with the standards on slide 21, whether car makers accept it without voiding warranties, and trial results. Amber is both a backer and the operator of an ARENA-supported V2G trial, so its results are worth following.

## Slide 28: Three questions, three answers
Will EV uptake overwhelm the transition? No. EVs are 5–12% of SWIS consumption by 2035; timing matters more than volume (net peak effect −2% to +3%).
Will EVs delay coal exit or lock in gas? No. Coal exit is a policy and economics decision; daytime-charged EVs help by absorbing solar. Evening charging would raise, not create, the firming task.
Is V2H / V2G essential? Not essential. Smart one-way charging delivers most of the benefit now; V2H is a useful resilience option; V2G is an upside to plan for, not a dependency.
What SEN should model next: SIREN scenarios: unmanaged vs managed vs V2G charging profiles against the coal-exit timeline
Notes: Three questions, three answers.
1. Will EV uptake overwhelm the transition? No. EVs are 5 to 12% of SWIS consumption by 2035, and the ESOO already allows for about 2 TWh of that. Timing matters more than volume: swapping scenarios moves the peak by minus 2% to plus 3%.
2. Will EVs delay coal exit or lock in gas? No. Coal exit is a policy and economics decision (Collie late 2027, Muja D late 2029). Daytime-charged EVs help by absorbing solar; evening charging would raise, not create, the firming task. The one thing still missing behind this answer is the SIREN run flagged on slide 11.
3. Is V2H / V2G essential? Not essential. Smart one-way charging delivers most of the benefit now, at roughly a fifth to a third of the installed cost of bidirectional hardware (slide 22). V2H is a useful resilience option, and V2G is an upside to plan for, not a dependency. Cost is the main barrier, and low-cost options such as V2G-Key (slide 23) are still in development.
What SEN should model next: SIREN scenarios comparing unmanaged, managed and V2G charging profiles against the coal-exit timeline. The ESOO scenario builder and the EV scenario page can support this: the EV page now uses the same 2025 IASR WEM trajectories as slides 6 to 9 and has a 'Net of ESOO's own EV load' option, so its numbers will match this deck. ESOO base scenarios built before the time-zone fix need rebuilding first.

## Slide 29: Thank you
sen.asn.au | info@sen.asn.au
Sustainable Energy Now Inc.
Notes: Thank you. Contact: sen.asn.au, info@sen.asn.au.
Likely questions and where the answer is: 'Why not just add EVs to the ESOO?' (slides 6 and 7: double counting). 'Is this the WEM or the NEM?' (WEM: slide 3 notes). 'What is the peak day?' (slides 8 and 9: synthetic, illustrative). 'How sure are the scenario mappings?' (slide 7: the Step Change link is an inference; the charging mix is assumed).